| Please check the following points before contacting us. Thank you. |
| --- |
| Headings | Customer |  | Contact |  | Tel.No. |  |
|  | Error description |  |
|  | When did the problem occur? |  | How long is plant already in operation? |  |
|  | Fan Art.No. |  | Fan type |  |
|  | Number of incorrect fans / total fans |  | Serial number motor |  |
|  | Order number |  | Motor PPA-Nr. |  |
|  | Site |  | Application (e.g. kitchen) |  |
|  | Finished Troubleshooting from the manual? | Y  | N  |
| Electrical | Electrical testing |
|  | Did you check the power supply directly on the fan? (3 phase) | Polarity and voltage of set point OK? (0 > X < +11VDC) | Could you measure the 24 V and 10 V voltage output from the fan? | No parallel wiring between 24 V and 10 V in multiple fans systems | Could you analyze the fan with ECParam over RS485? (PC / Connection / Converter) | miscellaneous: |
|  | Y  | N  | Y  | N  | Y  | N  | Y  | N  | Y  | N  |  |
|  | Questions about the electrical connection (Power Supply) |
|  | Test minimal configuration (Set point, Enable, see manual)? | Power supply from public network (TN-net)? | Correct power supply? According to Type plate? | Grounding of fan complete and correct? | Control voltage is laid in a separately cable? | Any high voltage testing’s made from customer? |
|  | Y  | N  | Y  | N  | Y  | N  | Y  | N  | Y  | N  | Y  | N  |
|  | Questions about the electrical connection (Control Voltage) |
|  | Operating mode / Circuit diagram Nr. | Set point 0-10 V DC (incl. GND) | Voltage between external GND and PE <15 V | Voltage supply for Enable from | Voltage on open contact, alarm relay? | miscellaneous: |
|  | Control-, Regulation-, Bus mode |  | Poti External 4-20 mA … |  | Y  | N  | fan 24 VDC external 24 VDC … |  | U= | Voltage ACDC |  |
| Mechanical | Questions for the application |
|  | AHU manufacturer | Type of installation | Clean and non-aggressive air (i.e. no kitchen exhaust, dust) | Airstream temperature < value on name plate | Space for Air-Out-Flow > 1,5*D Impeller Ø | Space for Air-In-Flow > 0,5*D Impeller Ø |
|  | Ros |  | Inside | Outside | Y  | N  | Y  | N  | Y  | N  | Y  | N  |
|  | Installation of the fan ( Electronic | Built in components | Humidity < 95 % | miscellaneous: |
|  | above | lateral | below |  | Heat recovery | Bypass | Heater | Chiller | Y  | N  |  |
|  | Questions about the tightness of the electrical connection |
|  | Cable gland firmly applied | Terminal area lid firmly applied | No dirt or cable remains below the lid | original cable gland | Flat sealing on gland present | miscellaneous: |
|  | Y  | N  | Y  | N  | Y  | N  | Y  | N  | Y  | N  |  |
|  | Questions to the fan | Extended Support (Remote Diagnosis) ( EC-support@rosenberg-gmbh.com |
|  | Fan Sound levels | Packaging OK | 1) This sheet filled out completely. | 2) Images (fan name plate, motor name plate, Electrical connection, Installation situation, Application, Wiring diagram…) | 3) Connect ECParam via a USB-RS485 Converter (H55-00054) and read out the Parameter-File and save a Log file if possible. | 4) If possible provide a video of the fan failure behavior. |
|  | Bearing damage Unbalance Balancing weights Grinding noises Transport damage … |  | Yes Damaged Wet … |  |  |  |  |  |
| Conclusion | Accomplished Actions |
|  | No actions necessary | Correct the connecting | ECParam | Flashing Firmware | Change electronic | Replace the fan |
|  | Other |
|  | Date: _______________ Signature (legible): ________________________ |